TABLE 22

NON-RADIOACTIVE COMPONENT OF LIQUID EFFLUENT 

DISCHARGED TO THE SYDNEY WATER SEWER, 

February 1995 – December 1999 

Component mg/L
YEARLY AVERAGE (1)
AVERAGE 1996 to 1999
Standard for Acceptance mg/L (2,3)


1996
1997
1998
1999



Suspended Solids
23
22
22
19
22
200 

pH
7.2
7.3
7.6
7.3
7.4
7 – 10

Ammonia
17.8
16.0
10.7
10
13.6
50 

BOD
36
23
12
14
21 
    85 (4)

Grease
14
13
12
7
12 
50 

Chromium
1.34
1.36
1.18
0.76
1.16
3 

Notes:

1. When calculating averages, “<” values were included, therefore the yearly averages are slightly overestimated.

2. Each month, a composite sample was collected from the effluent discharge pipeline (over a single production day). The following day, four geometric mean samples (collected at 2-hour intervals over the production day) were also collected. These five samples were analysed for their non-radioactive components.

3. 95% of all samples analysed must be less than or equal to the Standards for Acceptance of Liquid Trade Wastes to Sewers, specified in the Sydney Water Trade Waste Policy & Management Plan, 1995. 

4. The Standards for Acceptance do not stipulate a specific limit for BOD acceptance to all sewers, therefore the agreed limit is applicable in this case.

