TABLE 5. NON-RADIOACTIVE COMPONENTS OF LIQUID EFFLUENT

DISCHARGED TO THE SYDNEY WATER SEWER, LHSTC, July 2003 to June 2004
	Parameter
	 Concentration (mg/L)
July 2003 to June 2004
	Standard for Acceptance

(mg/L)

	
	Mean 
	Median
	Range
	

	Suspended Solids
	23.8
	13.0
	2 - 135
	600

	pH
	7.2
	7.1
	6.5 – 10.0
	7 – 10

	Ammonia
	11.8
	12.2
	< 0.5 – 26.2
	50

	BOD 
	18.3
	15.0
	3.0 – 55.0
	230

	Grease
	5.5
	5.0
	< 5 - 12
	110

	Zinc
	0.1
	0.1
	 < 0.1 – 1.1
	5

	Total Dissolved Solids
	354
	364
	226 - 482
	10 000


Notes:

1. The discharge of effluent to sewer is governed by an agreement between ANSTO and the Sydney Water Corporation: Consent to Discharge Industrial Trade Wastewater (Consent number 4423), Dec. 2003. The effluent is sampled every 4th discharge day. Of the samples analysed, 95% must be less than or equal to the Standards for Acceptance. 

2. The domestic concentration applies for biological oxygen demand (BOD).

3. Total Dissolved Solids were measured from January 2004 in accordance with the December 2003 trade waste agreement.

