TABLE 6

NON-RADIOACTIVE COMPONENTS OF LIQUID EFFLUENT

DISCHARGED TO THE SYDNEY WATER SEWER, LHSTC, January 2002 to June 2003

Parameter
 Concentration (mg/L)
January 2002 – June 2003
Standard for Acceptance

     mg/L (2)


Mean (1)
Median
Range


Suspended Solids
24
16
< 1 - 93
600

pH
7.2
7.3
5.2 - 9.9
7 – 10

Ammonia
9.6
8.6
< 0.5 - 38.7
100

B.O.D. (3)
20.1
14
< 2 - 148
   85 (3)

Grease
7.6
5
< 5 - 57
50

Zinc
0.2
0.2
 < 0.1 – 0.7
5

Notes:

1. The annual mean is conservative because results that were below the detection limits were included. 

2. The sampling regime was every 4 days from 1 July 2002, when the Sydney Water Trade Wastewater Agreement was renegotiated. Of the samples analysed, 95% must be less than or equal to the Standards for Acceptance of Liquid Trade Wastes to Sewers, specified in the Sydney Water Trade Waste Policy and Management Plan (1995). 

3. The standards for acceptance do not stipulate a specific limit for biological oxygen demand (BOD), therefore the agreed limit is applicable in this case.

