ANSTO E-745


TABLE 7a

TRITIUM IN COMPOSITE WATER SAMPLES FROM LHSTC 

STORMWATER BUNDS,  2000

Month
Total Volume collected 

(L)
TRITIUM (1)    (Bq/L)



BUND A (2,3)
Behind Building 1
BUND B

Opposite Meteorology Tower
BUND C

MDP – Waste Management Area

January
19
500 ( 30  
 -
 -

February
20
810 ( 10
 -
 -

March
25
2760 ( 30
1240 ( 10
90 ( 10

April
17
970 ( 20
220 ( 10
100 ( 10

May
23
400 ( 10
120 ( 10
100 ( 10

June
21
80 ( 10
70 ( 10
60 ( 10

July
19
320 ( 10
300 ( 20
100 ( 10

August
23
150 ( 10
120 ( 20
100 ( 10

September
20
160 ( 20
120 ( 10
80 ( 20

October
21
470 ( 10
90 ( 10
70 ( 10

November
22
170 ( 20
70 ( 10
120 ( 10

December
19
150 ( 20
100 ( 20
80 ( 20

Notes:

1. The WHO reference concentration for tritium in drinking water is 7800 Bq/L.

2. Refer to Figure 2 for the locations of the bunds. 

3. The sampling regime for Bund A in 2000 was changed to the following: 1 litre collected daily before the bund was discharged (except weekends and public holidays). These daily samples were combined to form a monthly composite for tritium analysis. This new sampling regime was extended to all three bunds in March and replaces the discrete samples collected once per month in previous years.

ENVIRONMENTAL and EFFLUENT MONITORING at ANSTO SITES, 2000

45


